## Slide 1
Tripura State Electricity Corporation Ltd.
(A Govt. of Tripura Enterprise)
Power Portfolio Management : Tripura
24.06.2026

## Slide 2
Presentation Flow
Present Power Scenario
Load Forecasting & Demand Projection
Resource Adequacy Plan

## Slide 3
Tripura Power Scenario (Present): Supply & Demand
Peak Demand : 542 MW
Total Availability: 410 MW
Intra-State Genr: 100 MW
Allocation from ISGS: 310 MW
Power Market: 132 MW
Solar Capacity: 103 MW
  Roof Top Solar: 53 MW
  Solar ISGS: 50 MW
Energy requirement: 1900 MU/Yr

## Slide 4
Tripura Power Scenario (Present): Transmission
132 KV Line: 987 Ckm
66 KV Line: 360 Ckm
132 KV Sub-station: 1522 MVA (21 nos.)
Transmission availability: 97%
Transmission Reliability: 2.5 trippings/line

## Slide 5
Tripura Power Scenario (Present): Distribution
Distribution Line
    33 KV: 1086 ckm
    11kV : 20,540 ckm
    LT : 34,857 ckm
Substation
  33/11kV : 86 Nos. (775 MVA)
  DT: 21,724 Nos. (1,616 MVA)
Consumers: 10,64,258 Nos.
Domestic Consumer : 88%
HT : 3.5%
AT&C Losses: 18.23% as on 31.03.2026
Chart: Consumer Profile (Consumption)
| Domestic | Commercial | Industries | Irrigation & Water | Public water works | Others
 | 681.1898 | 89.9304 | 50.0762 | 64.5119 | 175.8145 | 308.8778

## Slide 6
3 Seasons Load Curve
Chart: 
| 0000-0100 Hrs | 0100 -0200 Hrs | 0200-0300 Hrs | 0300-0400 Hrs | 0400-0500 Hrs | 0500-0600 Hrs | 0600-0700 Hrs | 0700-0800 Hrs | 0800-0900 Hrs | 0900-1000 Hrs | 1000-1100 Hrs | 1100-1200 Hrs | 1200-1300 Hrs | 1300-1400 Hrs | 1400-1500 Hrs | 1500-1600 Hrs | 1600-1700 Hrs | 1700-1800 Hrs | 1800-1900 Hrs | 1900-2000 Hrs | 2000-2100 Hrs | 2100-2200 Hrs | 2200-2300 Hrs | 2300-2400 Hrs
Winter | 132.6 | 121.025 | 118.275 | 114.575 | 116.975 | 122.35 | 158.7 | 206.825 | 220.875 | 208.3 | 185.525 | 184.5 | 183.9 | 174 | 170.525 | 157.45 | 177.325 | 238.65 | 226.875 | 223.8 | 216.325 | 199.225 | 173.325 | 151.05
Summer | 289.05 | 273.625 | 259.575 | 250.725 | 235.125 | 222.65 | 235.5 | 265.175 | 276.7 | 268.25 | 272.05 | 275.225 | 287.85 | 290.175 | 295.3 | 301.45 | 299.775 | 307.425 | 356.775 | 351.275 | 351.15 | 325.5 | 312.925 | 313.525
Rainy | 113.625 | 93.575 | 84.9 | 81.8 | 76.825 | 89.8 | 96.275 | 105.5 | 102.4 | 111.9 | 110.025 | 114.225 | 115.625 | 114.3 | 116.25 | 123.975 | 120.85 | 159.925 | 183.075 | 184.825 | 185.45 | 168.125 | 152.05 | 131.95
Tripura Seasonal Load Curve

## Slide 7
Monthly Peak Demand - Supply Scenario
Chart: DEMAND VS. AVAILABILITY (PEAK)
| 45748 | 45778 | 45809 | 45839 | 45870 | 45901 | 45931 | 45962 | 45992 | 46023 | 46054 | 46082
Own Generation | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
Central Sector | 301 | 301 | 301 | 325.5 | 325.5 | 325.5 | 325.5 | 325.5 | 325.5 | 325.5 | 325.5 | 325.5
Short-Fall | 55 | 71 | 54 | 35.5 | 22.5 | 61.5 | 24.5 | 0 | 0 | 0 | 0 | 0
Surplus | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -7.5 | -72.5 | -77.5 | -75.5 | -35.5
State Demand | 366 | 382 | 365 | 371 | 358 | 397 | 360 | 328 | 263 | 258 | 260 | 300
Total Demand I/c Cross-Border | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
OWN GENERATION
ISGS
SHORT-FALL
SURPLUS POWER
TOTAL I/C CROSS-BORDER
STATE DEMAND

## Slide 8
3 Seasons Load Curve
Load Research
Key Parameters Monitored Daily
  Entitlement for ISGS share → Allocation from central generating stations
  Previous day drawal → Actual vs scheduled consumption
  Bangladesh drawal → Cross‑border exchange tracking
  State generation → Output from state plants
  Shutdown of state line & impact → Transmission outages and reliability effects
  System Stability & Market Signals
  Frequency pattern → Monitoring deviations around 50 Hz
  RTM activities → Real‑time market trades for balancing demand
  DSM pattern → Settlement of deviations from schedule

## Slide 9
3 Seasons Load Curve
Daily Load Research and Demand Projection-Practice
Assimilate historical load data from SCADA/SLDC for last 3 years.
Collection of 33kV substation wise past loading profile.
Analysis of previous day demand pattern (96 blocks) and corresponding day demand of the last 3 years.
Review of weather conditions and forecast.
Energy Efficiency measures & Demand Side Management

## Slide 10
3 Seasons Load Curve
Daily Load Research and Demand Projection-Practice
Consideration of weekday, weekends, holiday and special events.
Assessment of expected State and renewable generation (Rooftop Solar).
Transmission constraint both inter and intra-state system.
Estimation of peak demand and daily energy requirement.
Preparation of Day-Ahead Forecast for scheduling and market participation.

## Slide 11
3 Seasons Load Curve
Balancing Mechanism
  Demand–Supply Balancing Methodology
  Weather report → Rainfall/temperature forecasts impacting demand & hydro inflows
  Load forecast → Anticipated demand for upcoming hours/days
  Backdown of generation → Curtailments due to surplus or constraints
  URS power → Un-requisition surplus available for scheduling of any generating station.
  Surrender of power → Relinquished share due to low demand or cheaper alternatives.

## Slide 12
3 Seasons Load Curve
Power Portfolio Management
Load Forecast & Weather Assessment
Resource Assessment
Demand–Supply Gap Analysis
DAM Participation
Day-Ahead Scheduling
Real-Time Monitoring
RTM Participation
DSM Management
Minimize Deviation Charges
Assess Available Power Resources
(ISGS + State Generation + RE + URS)
Surplus Power?
Power Deficit?
Yes
Yes
Assess Backdown
/ Surrender Opportunity
Participate in DAM
for Day-Ahead Requirement
Demand / Generation Deviation
NO
Yes
Post-Operation Performance Review
(DAM, RTM, DSM, Cost Optimization Analysis)
END
Start

## Slide 13
Year | Particulars | April | May | June | July | August | Sept | Oct | Nov | Dec | Jan | Feb | March
2025-26 | State Peak Demand (actual) | 334.30 | 347.10 | 336.09 | 374.47 | 362.00 | 376.91 | 346.89 | 310.09 | 240.35 | 237.20 | 246.47 | 289.30
2026-27 | State Peak Demand (Projection) | 344.33 | 351.20 | 365.90 | 385.70 | 372.86 | 388.22 | 357.30 | 319.39 | 247.56 | 244.32 | 253.86 | 297.98
2027-28 | State Peak Demand (Projection) | 354.66 | 361.74 | 376.88 | 397.28 | 384.05 | 399.86 | 368.02 | 328.97 | 254.99 | 251.65 | 261.48 | 306.92
2028-29 | State Peak Demand (Projection) | 365.30 | 372.59 | 388.18 | 409.19 | 395.57 | 411.86 | 379.06 | 338.84 | 262.64 | 259.19 | 269.32 | 316.13
Long-term Demand Projection

## Slide 14
Resource Adequacy Plan
Chart: Peak Demand & Energy Requirement Projection
| 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-30 | 2030-31 | 2031-32 | 2032-33 | 2033-34 | 2034-35 | 2035-36
Peak Electricity Demand Projected by 20th EPS (in MW) | 459 | 484 | 501 | 519 | 536 | 551 | 564 | 582 | 598 | 615 | 633
Electrical Energy Requirement Projected by 20th EPS (in MU) | 1926 | 2029 | 2131 | 2243 | 2352 | 2454 | 2551 | 2670 | 2784 | 2899 | 2988

## Slide 15
Resource Adequacy Plan …contd

## Slide 16
Resource Adequacy Plan …contd
Chart: Projected contracted capacity (MW) in 2035-36
| Coal | Gas | Hydro | Solar | PSP | BESS | DRE | SToA/MToA
 | 87 | 524 | 142 | 905 | 132 | 50 | 84 | 117

## Slide 17
Load Research & Demand Projection enabling power supply reliability
  Supply challenges due to increased penetration of Renewable capacity
  Continuous improvement in technique/process
  Optimisation of Power Portfolio Cost
  Capacity building
Summary

## Slide 18
Thank You
director.technical@tsecl.in